U-26003E-FM01B Boiler FD Fan Vibration Survey

Contents

Equipment Details	2

Machine Configuration	2

25.06.2020 PdM findings & equipment history (by Karrar):	4

16.07.2020 Motor solo run (By Mohammed):	6

18.07.2020 Alignment results (by Berik):	9

18.07.2020 (after-alignment survey by Mohammed) Fan found coupled.	10

Diagnosis & findings:	17

Recommendations:	17

U-26003E-FM01B Boiler FD Fan Vibration Survey

Equipment Details:

Motor details: AC induction motor, (25 Hz from spectral peaks with 1600 LOR)*60 = 1500 rpm

62 kW / 4 Poles

Vibration limits: ISO 10816-3 Group 2, rigid support.

Alert	4.5	mm/s rms

Danger	7.1	mm/s rms

|  |  | BPFO | BPFI | FTF | BSF |
| --- | --- | --- | --- | --- | --- |
| DE Bearing | 6318 C3 | 77.25 | 122.50 | 9.50 | 52.25 |
| NDE Bearing | 6318 C3 | 77.25 | 122.50 | 9.50 | 52.25 |
|  |  | 2XBPFO | 2XBPFI | 2XFTF | 2XBSF |
|  |  | 154.50 | 245.00 | 19.00 | 104.50 |
|  |  | 154.50 | 245.00 | 19.00 | 104.50 |

Blower details: 10 backward curved blades, CCW rotation.

Vibration limits: ISO 10816-3 Group 2, rigid support.

Alert	4.5	mm/s rms

Danger	7.1	mm/s rms

| Bearing pedestals |  | BPFO | BPFI | FTF | BSF |
| --- | --- | --- | --- | --- | --- |
| Radial (thrust) | 22217 | 114 | 160.75 | 10.25 | 71 |
| Bearing (thrust) | 22217 | 114 | 160.75 | 10.25 | 71 |
|  |  | 2XBPFO | 2XBPFI | 2XFTF | 2XBSF |
|  |  | 228.00 | 321.50 | 20.50 | 142.00 |
|  |  | 228.00 | 321.50 | 20.50 | 142.00 |

Machine Configuration (historical photos for adjacent equipment, same model)

25.06.2020 PdM findings & equipment history (by Karrar):

MOH: 1x dominant peak exceeding the alert limit.

MIH: 1x dominant peak exceeding the alert limit.

FIH: 1x dominant high peak below the alert limit.

16.07.2020 Motor solo run (By Mohammed): (Moderate levels)

| U-26003E-FM01B | MOH | MOV | MOA | MIA | MIH | MIV |
| --- | --- | --- | --- | --- | --- | --- |
| Vibrations mm/s RMS | 2.63 | 0.86 | - | 0.95 | 1.91 | 0.97 |
| Temperature Deg C | 51 |  |  | 52 |  |  |

18.07.2020 Alignment results (by Berik):

18.07.2020 (after-alignment survey by Mohammed) Fan found coupled.

| U-26003E-FM01B | MOH | MOV | MOA | MIA | MIH | MIV | FIA | FIH | FIV | FOA | FOH | FOV |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vibrations mm/s RMS | 6.21 | 1.99 | 3.26 | 2.78 | 4.88 | 2.09 | 1.79 | 2.79 | 2.58 | 2 | 1.48 | 2.79 |
| Temperature Deg C | 51 |  |  | 70 |  |  | 65 |  |  | 64 |  |  |

Equipment Spectra:

MOH: 1x high dominant peak, overall level is exceeding alert limit

MOV: 1x & 2x moderate dominant peaks. Low 3x peak Overall level is within limit

MOA: 1x & 2x moderate dominant peaks. Low 3x peak Overall level is within limit

Motor 3x

2x

MIA: 1x & (2x higher thank 1x) moderate dominant peaks. Low 3x peak Overall level is within limit

MIH: 1x high dominant peak, overall level is exceeding alert limit

Motor 3x

2x

MIV: 1x moderate dominant peak. Low 2x peak. Low 3x peak Overall level is within limit

3x

2x

1x

@13.8 Hz??

FIA with 1x Harmonics Cursers

FIA: moderate 1x and lows 1x harmonics. Low 3x peak Overall level is within limit

FIH: 1x high dominant peaks. Overall level is within limit

FIV: 1x moderate dominant peak. Low 2x peak. Overall level is within limit

FOA: moderate 1x peak. Low 2x. Low 1x harmonics. Low 3x peak Overall level is within limit

FOH: moderate dominant 1x peak. Low 1x harmonics. Overall level is within limit

FOV: moderate dominant 1x peak. Low 1x harmonics. Overall level is within limit

Phase measurement across coupling (ch1 FIH / ch2 MIH)	      Phase measurement across coupling (ch1 FIV / ch2 MIV)

Phase measurement across coupling (ch1 FIA / ch2 MIA)

Phase measurement between Ch1 MIH & Ch2 MIV	         Phase measurement between Ch1 MOH & Ch2 MOV

Diagnosis & findings:

- Motor Test run has not been carried out after finalizing the alignment.

- Rough rocking sound can be heard from the chassis space, fan inboard bearing is suspected to be the source.

- Louver hubs of the outlet check valve damper are not turning during the coast up and coast down (despite they are greased). Suspected to be stuck.

- Combination of a dynamic unbalance/Resonance is suspected from the phase readings between the H & V in each side and from the cross phase readings and the directional vibration amplification in the horizontal direction (in the motor, motor base & the fan bearings).

- Structural looseness is suspected as a source for the resonance excitation.

Recommendations:

- To tight all the structural bolts of the motor, fan pedestals, structural studs of the fan casing & all the joints.

- To decouple the motor and inspect coupling for any damages. Photos are required to prove that coupling is in healthy condition.

- To verify the alignment result (as found measurements are required) and to correct the misalignment, if needs to be.

- To perform soft foot check and correction. Should be followed by motor solo run.

- To perform motor solo test run with vibration measurements to verify the absence of a potential soft foot.

- To perform test run after the coupling installation

- If the high vibration still persisting, fan and casing internals are to be investigated.